## HVAC Cost Summary
HVAC 5BOD Phase 4 - Detailed Cost Breakdown (ROM)
Saga Pryor Data Center - 22 MW IT Load (29.7 MW Facility)
Category | Equipment Description | Quantity | Unit Cost | Extended Cost | Certainty | Notes
CHILLERS - L2C PLANT
L2C Air-Cooled Chillers | 1,500 kW, free-cooling capable | 12 units | 350000 | 4200000 | 0.6 | Based on $233/kW industry avg + 40% price escalation since 2021
CHILLERS - RDHx PLANT
RDHx Air-Cooled Chillers | 1,500 kW, free-cooling capable | 6 units | 350000 | 2100000 | 0.6 | Based on $233/kW industry avg + 40% price escalation since 2021
LIQUID COOLING DISTRIBUTION
CDUs (Coolant Distribution Units) | 100-120 kW capacity, A/B pairs | 324 units | 85000 |  | 0.5 | Based on $400-500/kW DTC cost range, high variability by vendor
RDHx Units | 25 kW rear-door exchangers | 232 units | 12000 |  | 0.55 | Estimated based on passive cooling tech, limited public pricing
GLYCOL SYSTEMS
Propylene Glycol (Bulk) | 25-30% concentration | 6,000 gal | 12 | 72000 | 0.85 | Market pricing Q1 2025: $11/gal bulk + delivery
Glycol Mix Tanks | 500 gal pre-mix stations | 3 units | 8000 | 24000 | 0.7 | Standard industrial tank + mixing equipment
Fill Stations | Transfer pumps, meters, valves | 3 units | 15000 | 45000 | 0.65 | Estimated based on pump + instrumentation package
Chemical Dosing Pots | Corrosion inhibitor injection | 3 units | 3500 | 10500 | 0.7 | Standard industrial dosing equipment
PIPING & DISTRIBUTION
Primary Loop Piping (Loop 3) | 6"-12" steel, insulated, supported | 3,000 LF | 180 | 540000 | 0.6 | Based on $150-200/LF for insulated industrial pipe
Primary Loop Piping (Loops 1+2) | 4"-8" steel, insulated, supported | 2,000 LF | 150 | 300000 | 0.6 | Smaller diameter, same spec as Loop 3
Secondary Loop Piping (L2C) | 1"-2" SS/dielectric-compatible | 5,000 LF | 120 | 600000 | 0.55 | Stainless steel + specialty fluid compatibility
Quick-Disconnect Couplings | Dry-break type, rack connections | 394 units | 800 | 315200 | 0.65 | Industrial quick-disconnect + installation
Isolation Ball Valves | Various sizes, major equipment | 100 units | 450 | 45000 | 0.7 | Standard industrial valve pricing
Expansion Tanks | 500-1,000 gal bladder-type | 3 units | 12000 | 36000 | 0.7 | Industrial expansion tank + installation
Air/Dirt Separators | Filtration + separation | 6 units | 6000 | 36000 | 0.7 | Standard HVAC accessories
LEAK DETECTION
Sensing Cable | Conductive fluid detection | 3,000 LF | 25 | 75000 | 0.75 | Standard leak detection cable pricing
Spot Leak Detectors | Discrete sensors | 500 units | 200 | 100000 | 0.75 | Commercial spot detector pricing
Control Panels | BACnet/IP integration, N+1 | 2 units | 35000 | 70000 | 0.7 | Industrial control panel + programming
DATA HALL ENVIRONMENTAL
DOAS Units | 100% OA, enthalpy wheel, N+1 | 4 units | 85000 | 340000 | 0.55 | Estimated based on high-capacity commercial units
Steam Humidifiers | Integrated with DOAS | 4 units | 12000 | 48000 | 0.7 | Standard steam injection humidifier
SUPPORT SPACE HVAC
Rooftop Units (RTUs) | Package DX units | 5 units | 35000 | 175000 | 0.7 | Commercial RTU pricing
Mechanical Room HVAC | Factory-integrated cooling | 5 units | 25000 | 125000 | 0.65 | Integrated UPS/electrical room cooling
SUBTOTAL - EQUIPMENT & MATERIALS |  |  |  | 9256700 | 0.58 | Average certainty across all line items
INSTALLATION LABOR | 35-45% of equipment cost |  |  | 3702680 | 0.5 | Industry standard range for complex systems
ENGINEERING & COMMISSIONING | 8-12% of installed cost |  |  | 925670 | 0.55 | Design, startup, testing, TAB
CONTINGENCY | 15% for BOD phase uncertainty |  |  | 1388505 |  | Recommended for pre-design phase
TOTAL MECHANICAL SYSTEMS (PHASE 4) |  |  |  | 15273555 | 0.55 | ROM estimate - budget quality only