## Change Log to Owner Project Requirements (OPR)

Document Reference: GGE-000-DES-PMG-0001_01

Revised Document Coding: GE01-DES-PM00-OPR-0001_02

Purpose: Accompany OPR submission to the Uptime Institute / Issued for Design (IFD)

Revision Target: 02

Date: October 30, 2025

Prepared By: Teymur Nasrullayev (Data Center Manager)

Approved By: Ramiz Mammadov (Chairman/Director)

### 1. Updates Based on Basis of Design (BoD)

- Cooling System Strategy: Confirmed hybrid cooling system using river-water free cooling and ground-thermal field. Supports PUE ≤ 1.5.

- Power Topology: Dual independent utility + HPP feeds, 2N transformer configuration, modular UPS with LiFePO₄ batteries.

- Mechanical Redundancy: N+1 dry coolers for GPU racks; auto-failover if river temperature exceeds 26°C.

- Certification Target: Tier III compliance confirmed with Tier IV-ready design features.

- Structural Zoning: Floor load capacities and slab-to-slab construction confirmed for critical zones.

- Energy Source: 3.7 MW Mtkvari HPP + city utility; 100% renewable baseline.

- IT Capacity Breakdown: 5.635 MW total; Quantum AI (2.5 MW), Enterprise Suites (1.47 MW), Hub (0.665 MW), VIP (1.0 MW).

### 2. Design Review Register-Driven Changes

- Security Booth Relocation: Lobby layout revised to position security booth closer to entrance.

- Mantrap Addition: Vestibule/mantrap added to main entrance with access control and intercom.

- Bullet-Resistant Glass: Security booth now includes impact/bullet-resistant glass.

- Oversized Doors: Clear door heights of 2.8–4.5 m confirmed for equipment access.

- Office Area Optimization: Office areas on IT floors reduced to prioritize critical space.

- Transformer Sizing: Transformer count reduced to align with actual IT load; future expansion space reserved.

- UPS Coverage: UPS protection extended to critical cooling equipment and BMS servers.

- Switchgear Layout: Electrical room layouts revised for efficiency and clarity.

- Cable Routing: UPS and switchgear proximity improved to reduce cable lengths.

- Corridor Strategy: Central corridor retained per Owner’s directive; external wall insulation improved.

- Room Labeling Corrections: ER-A and ER-B labeling errors corrected; ER-C added.

- Chiller Redundancy Clarification: Revised to reflect N+1 scalable to 2N, correcting overbuilt 2N installation.

### 3. Physical Security Design Framework Integration

- Security Zones Defined: Violet, Blue, Yellow, Orange, Red, and Black zones established with Control Points (CP1–CP5).

- Security Classification: Facility classified as EN 50600-2-5 Security Class 3.

- Multi-Factor Authentication (MFA): Mandatory biometric authentication (iris) for transitions into Orange and Red Zones. Facial recognition reserved for VIP entry.

- Visitor Management System (VMS): Integrated with ACS; strict ID policy and escorting rules enforced.

- Mantrap Protocols: Single-person entry enforced with dual authentication and CCTV coverage at 125 ppfw.

- Emergency Override Protocols: Fire alarm overrides all other protocols; lockdown, flood, earthquake, and battery incidents integrated with ERP.

- Security Control Room (SCR): Redundant systems, 72-hour sustainment capability, and integrated command protocol with NOC.

- CICO Checkpoint: Mandatory screening, asset logging, and tamper-evident seals for tools and equipment.

- Secure Network Infrastructure: Physically isolated, UPS-backed, monitored network for ACS, CCTV, IDS.

- Compliance & Governance: GDPR-compliant biometric and CCTV systems; DPIA and ROPA documentation mandated.

- Maintenance Protocols: Quarterly health checks, annual calibration, and 3-year log retention for all security systems.

- Supplier Vetting: ISO/IEC 27001-compliant supplier for lifecycle management and access control.

- Design Intent Handover: Formal process defined with certificate prerequisite for Security Operations Manual approval.

### 4. SSRP (Staffing Strategy & Recruitment Plan) Integration

- FTE Revision: Staffing reduced from 81 to 50 FTEs across 26 unique roles in 4 functional areas.

- Role Adjustments: CRCO removed; CISO scope expanded to include HPP; CCO now oversees SLA Team.

- Security Staffing: 12 Security Specialists moved to a subcontracting model.

- Recruitment Strategy: Dual-track approach—local recruitment for junior roles, international search for specialized positions.

- Training Standards: Tiered training structure (enterprise-wide, function-specific, role-specific) aligned with Tier III, ISO 27001, CDCP, CISSP, VCP.

- Governance: RACI model defined; quarterly reporting and KPI tracking implemented.

- Succession Planning: Framework mandated for mission-critical roles with career pathing and diversity goals.

- Diversity & Inclusion: Formal D&I targets, and inclusive sourcing channels established.

- Budgeting: Compensation benchmarking and budget planning tied to JD development.

- Recruitment Timeline: Phased hiring plan from Q1 2026 to Q2 2027.

### 5. Pre-Sales Engineering & Catalogue Alignment

- Service Enablement Systems: Engineering requirements mapped to catalogue offerings—DCIM, CRM, BMS, RMS, SIEM, VMS, API Gateway.

- Security Systems: SIEM, CCTV, Access Control, and VMS confirmed as high-priority foundational systems.

- Customer Support Platform: "Biliki.Support" platform defined for omni-channel support, SLA tracking, and infrastructure control.

- Infrastructure Monitoring: DCIM and BMS prioritized capacity planning and environmental control.

- Service Fulfillment: Automated orchestration platform required for Core Services provisioning.

- Compliance Mapping: ISO 27001, GDPR, NFPA, and EN 50600 standards integrated across service and infrastructure layers.

### 6. Updates Based on ERP, HSE Manual, and Legal & Compliance Assessment Report (LCAR)

- Emergency Preparedness Integration: ERP protocols for fire, incident, and evacuation incorporated into operational readiness.

- Mock Drill Protocols: Annual drills for offices/stores; quarterly for Data Center and HPP. Lessons learned to be documented.

- Emergency Roles Formalized: EC, ERO, ERS, Fire Wardens, and First Aiders roles defined with responsibilities and contact protocols.

- ERP–BCP–DR Transition: Formal handoff protocol established for seamless emergency-to-recovery transition.

- ESG Emergency Annex: Environmental (spill, flood), social (inclusive evacuation), and governance (incident KPIs, board oversight) safeguards embedded.

- HSE Governance: HSEQ Manager and HSE Board roles clarified; monthly review cycles and delegated authority for updates and audits.

- Training Matrix: HSE training matrix defined for all roles; includes emergency response, hazard awareness, and operational control procedures.

- Operational Control Procedures: Permit-to-work system, hazard elimination, and PPE provisioning formalized.

- Legal Compliance Tracking: Monthly legal compliance verification and register maintenance mandated.

- Contractor Safety Compliance: Contractors must undergo HSE induction and comply with Owner HSE standards; performance tracked via dedicated forms.

- ESHIA Adoption: ESHIA adopted as compliance baseline, exceeding Georgian EAC requirements by including SIA, HIA, SEP, and ESMP.

- Certification Alignment: Project design and documentation aligned with IFC PS, HSS, Verra VCS, and LEED frameworks.

- Gap Closure Strategy: Developer-led inputs (GHG modeling, biodiversity co-benefits, stakeholder benefit-sharing) identified for certification readiness.

- Scoping Decision Protocol: Voluntary EIA path confirmed; scoping decision to serve as binding ToR for ESHIA.

- Public Participation Enhancements: SEP and grievance mechanisms added to exceed EAC minimums and align with international standards.

### 7. Summary of Impact

These changes ensure:

- Full alignment with Tier III and Tier IV-ready design principles.

- Enhanced physical and cyber security posture.

- Compliance with international standards (ISO/IEC 27001, GDPR, EN 50600).

- Operational readiness and maintainability.

- Integration of ESG, staffing, and service delivery frameworks.